Galaxy Steam Boiler

Furnish and install, as shown on the plans, ____(Qty) Galaxy model GG______ gas-fired hot water boiler(s). These boilers shall have a CSA design certified input of _____Btuh, D.O.E. heating capacity of _____Btuh and a Net I=B=R rating of ______Btuh. The A.F.U.E. efficiency shall be ___%. (When boiler reaches 300,000 Btuh input AFUE efficiency is Thermal Efficiency and DOE Heating Capacity is Gross Output.)

Electrical service shall be 115 volt 60 hertz 1 phase. Boiler(s) shall be CSA designed certified. Factory supplied rating plate shall have CSA designed certified symbol and ASME “H” stamp. A low water cut-off shall be factory provided, installer shall install any additional items to satisfy local boiler code requirements.

Boiler(s) heat exchanger(s) shall be constructed of cast iron sections with casting assembly being clearly marked with the ASME symbol. Sections shall be assembled in accordance with ASME requirements using metal push nipple seals between the sections that will provide a permanent heat and chemical resistant seal, gasket or rubber seals are not acceptable. Maximum ASME working pressure steam shall be 15 PSI. Each section shall be hydrostatically tested at the foundry and casting assemblies hydrostatically tested on final assembly line in accordance with ASME Code. Boiler flues shall have cast iron thermal pins with a pattern that ensures uniform heat transfer.

Factory supplied A.S.M.E pop safety relief valve and pressure gauge must be supplied. Pop safety relief valve shall be rated at 15 P.S.I.

Boiler(s) shall be manufactured for use in a vent category I (chimney vented) application.

Boiler(s) flue collector shall be manufactures out of heavy gauge aluminized steel. The boiler base assembly shall be constructed of heavy gauge aluminized steel with thick refractory insulation on the inside. Burners shall be one piece stainless steel construction, aluminized steel is not acceptable. Each burner shall have an adjustable air shutter used to adjust the combustion as required. Burners without adjustable air shutters are not acceptable.

Boiler shall be equipped with a factory supplied PA404A pressure control, low water cut-off, water sight glass, pressure gauge, ASME 15 PSI steam pressure relief valve, drain valve, flame rollout switch and draft hood equipped with a blocked vent swith that interrupts power to the gas valve in the event of a related unsafe condition.

Optional Tankless DHW Coil: Boiler shall have a factory installed tankless domestic hot water heater coil that supplies ____ gallons per minute of domestic hot water based on intermittent draw. Boiler shall have a low water temperature control to maintain boiler temperature to supply DHW.

Ignition shall be accomplished through intermittent pilot spark ignition; hot surface ignition is not acceptable. Pilot shall be burner mounted to facilitate accurate location of pilot for smooth ignition of main burner.

Boiler jacket shall be, durable painted steel, insulated and factory installed.

Installer shall install and test fire boiler(s) in accordance with manufacturer’s installation instructions and local authority requirements.

Installer shall install and test fire boiler(s) in accordance with manufacturer’s installation instructions and local authority requirements.

Steam Boiler shall have a 10 year warranty on the cast iron heat exchanger and a 1 year from date of installation warranty on all factory supplied parts and controls.

616