Jaguar J-390 Series

Furnish and install, as shown on the plans, ____(Qty) Jaguar Model J-390 natural gas-fired water boiler(s). The (These) boiler(s) shall have a CSA design certified maximum input of 390,000 Btuh, minimum input of 110,000 Btuh: a maximum Gross Output of 352,000 Btuh, Net I=B=R rating of 306,000 Btuh. Boiler input shall modulate between the maximum and minimum input as controlled by factory mounted and tested boiler control. The boiler control will automatically modulate input to closely match actual load

Electrical service shall be 115 volt 60 hertz 1 phase. Boiler shall be CSA design certified. Factory supply rating plate shall have CSA design certified symbol and ASME “H” stamp. Installer shall provide and install low water cut-off, manual reset hi-limit control and any additional items to satisfy code requirements.

Boiler ignition shall be direct spark. Factory installed solid state ignition/boiler control mounted with the control not exposed to boiler combustion air intake, boilers with the control mounted within an enclosure where the control is exposed to sealed combustion incoming outdoor air are not acceptable. Boiler control shall constantly monitor boiler operation. Boiler control shall manage light off, combustion, boiler input and desired supply water temperature. Control shall have built-in outdoor reset for modulating system water temperature. Control shall have ability set priority on set point temperature or outdoor reset temperature. Set-up and programming of boiler control shall be accomplished from top front of boiler. Control shall have diagnostic codes to identify problems.

Boiler burner shall be woven metal fiber pre mix to facilitate clean combustion with variable fuel input. Gas valve shall be negative regulated redundant factory mounted on variable speed combustion blower with matching venturi to maintain proper air/fuel mixture throughout boiler’s design modulating fuel input. Boiler fuel input shall modulate between maximum and minimum fuel inputs, step firing is not acceptable. Ignition shall be direct spark, hot surface ignitors are not acceptable. Boiler shall fire under middle input for smooth and quiet ignition. Boiler shall be natural gas fired.

Boiler heat exchanger shall be constructed of a cast aluminum mono block for high thermal conductivity heat exchange, resistance to corrosion due to flue product condensation and durability. Maximum working pressure is 30 PSI. Heat exchanger shall be factory tested in accordance with ASME code. Factory supplied ASME safety relief valve shall be supplied by the factory. The safety relief valve shall be rated at 30 PSI.

Boiler shall be manufactured for use in a sealed combustion, direct vent application. Boiler shall be approved for air intake using 4 inch nominal schedule 40 PVC, schedule 40 CPVC or stainless steel pipe. Boiler shall be approved for exhaust vent using 4 inch nominal schedule 40 PVC, schedule 40 CPVC or stainless steel pipe. Foam core pipe is not acceptable. Air intake, exhaust vent and vent terminations shall be installed in accordance with manufacturers instructions as well as code requirements.

Boiler shall have two factory installed drains for condensate removal. One shall be for condensate collected on the boiler heat exchanger. The second shall be a exhaust vent condensate drain to prevent corrosive exhaust vent condensate from draining back to the boiler heat exchanger and accelerate heat exchanger deterioration while lowering heat exchange efficiency for the boiler. These two condensate drains shall be factory mounted and connected to a common drain on the boiler. Condensate drains shall have a factory mounted trap to prevent products of combustion from leaking into the boiler room. Condensate is acidic and shall be naturalized by a field supplied neutralizer.

Installing contractor shall perform system start up in accordance with manufacturer’s instructions and code requirements. This shall include safety check on operation of all system and safety controls as well as boiler set up with combustion analyzer.