Victory II Series

Furnish and install, as shown on the plans, ____(Qty) Victory model VHS-______ gas-fired hot water boiler(s). The (These) boiler(s) shall have a CSA design certified input of _____Btuh, D.O.E. heating capacity of _____Btuh and a Net I=B=R rating of ______Btuh. The A.F.U.E. efficiency shall be ___%.

Electrical service shall be 115 volt 60 hertz 1 phase. Boiler shall be CSA designed certified. Factory supplied rating plate shall have CSA designed certified symbol and ASME “H” stamp. If required, installer shall provide low water cut-off, additional hi-limit control and any additional items to satisfy local code requirements.

Boiler heat exchanger shall be constructed of cast iron sections with casting assembly being clearly marked with the ASME symbol. Sections shall be assembled in accordance with ASME requirements using metal push nipple seals between the sections that will provide a permanent heat and chemical resistant seal, gasket or rubber seals are not acceptable. Maximum ASME working pressure shall be 50 PSI. Each section shall be hydrostatically tested at the foundry and casting assemblies hydrostatically tested on final assembly line in accordance with ASME Code. Casting assemblies shall be hydrostatically tested at the factory a third time to ensure quality. Boiler flues shall have cast iron thermal pins with a pattern that ensures uniform heat transfer.

Factory supplied A.S.M.E. safety relief valve and a pressure/temperature gauge must be supplied. Safety relief valve shall be rated at 30 P.S.I.

Boiler shall be manufactured for use in power vent application. Boiler shall be induced draft and products of combustion shall be vented outside using approved AL29-4C stainless steel vent material in accordance with boiler manufacturer’s instructions. Induced draft blower shall have factory installed flue gas condensate drain with trapped condensate drain. Redundant 100% shutoff gas valve shall be used. Ignition shall be intermittent pilot that is lighted by spark; hot surface ignition is not acceptable. To ensure proper air flow for combustion the boiler shall have a factory installed air flow proving switch. A factory installed burner flame roll out safety switch is required.

Boiler flue collector shall be manufactured out of heavy gauge aluminized steel. The boiler base assembly shall be constructed of heavy gauge aluminized steel with thick refractory insulation on the inside. Burners shall be one-piece stainless steel with adjustable air shutters for primary combustion air.

Boiler jacket shall be insulated, painted steel and factory installed.

Installer shall install and test fire boiler in accordance with manufacturer’s installation instructions and local authority requirements.

Installer shall place the boiler owners manual, installation instructions and replacement parts list in a conspicuous location close to the boiler.